## EV Sizing
(From water at 15C) |  | Calcs based on Avg. of Flow&return hot water at 60C
Water |  | System or HWC capacity | 85 | Litres
Temp | Exp | Exp. Vessel Capacity | 12 | Litres
Deg.C | % | Pre Charge Pressure | 0.75 | Bar.G
50 | 1.124 | Pre Charge Pressure | 1.75 | Bar.A | Change values in Yellow only
60 | 1.62 | Filling/supply Pressure | 1 | Bar.G
65 | 1.83 | Filling Pressure | 2 | Bar.A | Boiler Heating System
70 | 2.18 | Air Space Vol | 10.5 | Litres | Note: The filling pressure should be 0.3/0.5bar higher than the pre charge
75 | 2.48 | Reserve Water Vol | 1.5 | Litres | pressure as this gives a small water reserve when cold and avoids frequent
80 | 2.8 | Expansion % | 1.62 | % | top ups. This must be taken into account when sizing the E.vessel.
85 | 3.13 | Expansion | 1.377 | Litres
90 | 3.49 | Water Space Vol | 2.877 | Litres | When calculating the expansion volume %, use the average of the
95 | 3.85 | Air Space Vol | 9.123 | Litres | boiler flow&return temperatures.
100 | 4.24 | Final Pressure | 2.3019 | Bar.A
105 | 4.64 | Final Pressure | 1.3019 | Bar.G | Some boiler manufacturers now including Grant specify a
110 | 5.05 |  |  |  | 2.5 Bar PRV, this was normally 3.0 Bar, this must be taken
|  | System or HWC capacity | 85 | Litres | into account when sizing the expansion vessel.
|  | Exp. Vessel Capacity | 12 | Litres
|  | Pre Charge Pressure | 1 | Bar.G | NB: The filling pressure must not be lower than the pre charge pressure (the calculation
|  | Pre Charge Pressure | 2 | Bar.A | will also be incorrect ), it must always be = to or> than the pre charge pressure.
|  | Filling/supply Pressure | 1.5 | Bar.G
|  | Filling Pressure | 2.5 | Bar.A
|  | Air Space Vol | 9.6 | Litres
|  | Reserve Water Vol | 2.4 | Litres
|  | Expansion % | 1.62 | %
|  | Expansion | 1.377 | Litres
|  | Water Space Vol | 3.777 | Litres
|  | Air Space Vol | 8.223 | Litres
|  | Final Pressure | 2.9186 | Bar.A
|  | Final Pressure | 1.9186 | Bar.G