## EV Sizing
Values in yellow may be changed
| From | From | From | System or HWC capacity | 250 | Litres |  | S.sheet protected but not password protected
| Water | Water | Water | Exp. Vessel Capacity | 25 | Litres | 10% | Numbers in yellow may be changed with protection On.
Water | at 5C | at 10C | at 15C | Pre Charge Pressure | 1.8 | Bar.g |  | If S.sheet format needs changing, right click on sheet "EV Sizing" (below left) and
Temp | Exp | Exp | Exp | Pre Charge Pressure | 2.8 | Bar.a |  | select "unprotect sheet" from the drop down menu.
Deg.C | % | % | % | Filling/supply Pressure | 2 | Bar.g
40 | 0.782 | 0.757 | 0.695 | Filling Pressure | 3 | Bar.a |  | Boiler Heating System
45 | 0.986 | 0.96 | 0.899 | Air Space Vol | 23.3333 | Litres |  | Note: The precharge pressure should never be higher than the filling pressure
50 | 1.21 | 1.182 | 1.124 | Reserve Water Vol | 1.6667 | Litres |  | but where fitted to a boiler should be set 0.3/0.5 bar lower than the filling
55 | 1.45 | 1.422 | 1.36 | Expansion % | 1.98 | % |  | pressure as this gives a small water reserve when cold and avoids frequent
60 | 1.71 | 1.68 | 1.62 | Expansion | 4.95 | Litres |  | top ups. This must be taken into account when sizing the E.vessel.
65 | 1.98 | 1.954 | 1.83 | Water Space Vol | 6.6167 | Litres |  | When calculating the expansion volume %, use the average of the
70 | 2.27 | 2.245 | 2.18 | Air Space Vol | 18.3833 | Litres |  | boiler flow&return temperatures. (CH System)
75 | 2.58 | 2.551 | 2.48 | Final Pressure | 3.8078 | Bar.a
80 | 2.9 | 2.873 | 2.81 | Final Pressure | 2.8078 | Bar.g |  | UV Cylinder
85 | 3.238 | 3.21 | 3.13 |  |  |  |  | It's recommended to set the precharge pressure 0.2/0.5bar lower than the
90 | 3.59 | 3.563 | 3.49 |  |  |  |  | than the filling (PRV) pressure, this helps to prevent the diaphragm bottomimg out
95 | 3.959 | 3.931 | 3.85 |  |  |  |  | and some say helps to prevent water hammer
100 | 4.342 | 4.315 | 4.24
105 | 4.741 | 4.714 | 4.64

## Configuration
|  |  |  | From | From | From
|  |  |  | Water | Water | Water | Boiler Heating System
System or HWC capacity | 85 | Litres | Water | at 5C | at 10C | at 15C | Note: The precharge pressure should never be higher than the filling pressure
Exp. Vessel Capacity | 8 | Litres | Temp | Exp | Exp | Exp | but where fitted to a boiler should be set 0.3/0.5 bar lower than the filling
Pre Charge Pressure | 1 | Bar.g | Deg.C | % | % | % | pressure as this gives a small water reserve when cold and avoids frequent
Pre Charge Pressure | 2 | Bar.a | 40 | 0.782 | 0.757 | 0.695 | top ups. This must be taken into account when sizing the E.vessel.
Filling/supply Pressure | 1.5 | Bar.g | 45 | 0.986 | 0.96 | 0.899 | When calculating the expansion volume %, use the average of the
Filling Pressure | 2.5 | Bar.a | 50 | 1.21 | 1.182 | 1.124 | boiler flow&return temperatures. (CH System)
Air Space Vol | 6.4 | Litres | 55 | 1.45 | 1.422 | 1.36
Reserve Water Vol | 1.6 | Litres | 60 | 1.71 | 1.68 | 1.62 | UV Cylinder
Expansion % | 1.98 | % | 65 | 1.98 | 1.954 | 1.83 | It's recommended to set the precharge pressure 0.2/0.5bar lower than the
Expansion | 1.683 | Litres | 70 | 2.27 | 2.245 | 2.18 | than the filling (PRV) pressure, this helps to prevent the diaphragm bottomimg out
Water Space Vol | 3.283 | Litres | 75 | 2.58 | 2.551 | 2.48 | and some say helps to prevent water hammer
Air Space Vol | 4.717 | Litres | 80 | 2.9 | 2.873 | 2.81
Final Pressure | 3.392 | Bar.a | 85 | 3.238 | 3.21 | 3.13
Final Pressure | 2.392 | Bar.g | 90 | 3.59 | 3.563 | 3.49
|  |  | 95 | 3.959 | 3.931 | 3.85
|  |  | 100 | 4.342 | 4.315 | 4.24
|  |  | 105 | 4.741 | 4.714 | 4.64