## EV & Air Bubble
(From water at 15C) |  | UVC with Expansion Vessel |  |  |  | values in yellow may be changed
Water |  | System or HWC capacity | 200 | Litres |  | S.sheet protected but not password protected
Temp | Exp | Exp. Vessel Capacity | 20 | Litres |  | Numbers in yellow may be changed with Protection ON.
Deg.C | % | Pre Charge Pressure | 2.8 | Bar.G |  | If s.sheet format needs changing, right click on "EV & Air Bubble, (below left) and
50 | 1.124 | Pre Charge Pressure | 3.8 | Bar.A |  | select "unprotect sheet" from the drop down menu.
60 | 1.62 | Filling/supply Pressure | 3 | Bar.G
65 | 1.83 | Filling Pressure | 4 | Bar.A | 2 | Boiler Heating System
70 | 2.18 | Air Space Vol | 19 | Litres |  | Note: The pre pressure should never be higher than the filling pressure
75 | 2.48 | Reserve Water Vol | 1 | Litres |  | but where fitted to a boiler should be set 0.3/0.5 bar lower than the filling
80 | 2.8 | Expansion % | 1.62 | % |  | pressure as this gives a small water reserve when cold and avoids frequent
85 | 3.13 | Expansion | 3.24 | Litres |  | top ups. This must be taken into account when sizing the E.vessel.
90 | 3.49 | Water Space Vol | 4.24 | Litres
95 | 3.85 | Air Space Vol | 15.76 | Litres |  | When calculating the expansion volume %, use the average of the
100 | 4.24 | Final Pressure | 4.8223 | Bar.A |  | boiler flow&return temperatures. (CH System)
105 | 4.64 | Final Pressure | 3.8223 | Bar.G
110 | 5.05 |  |  |  |  | Some boiler manufacturers now including Grant specify a
|  | UVC with Air Bubble. (Megaflo) |  |  |  | 2.5 Bar PRV, this was normally 3.0 Bar, this must be taken
|  | System or HWC capacity | 200 | Litres |  | into account when sizing the expansion vessel.
|  | Expansion Vol | 25 | %
|  | Air Space Vol | 50 | Litres |  | NB: The filling pressure must not be lower than the pre charge pressure (the calculation
|  | Water Volume | 150 | Litres |  | will also be incorrect ), it must always be = to or> than the pre charge pressure.
|  | Pre Charge Pressure | 0 | Bar.G
|  | Pre Charge Pressure | 1 | Bar.A
|  | Filling/supply Pressure | 3 | Bar.G
|  | Filling Pressure | 4 | Bar.A
|  | Air Space Vol | 12.5 | Litres
|  | Water Vol. Nominal | 187.5 | Litres
|  | Expansion % | 1.62 | %
|  | Expansion | 3.0375 | Litres
|  | Water Volume | 190.5375 | Litres
|  | Air Space Vol | 9.4625 | Litres
|  | Final Pressure | 5.284 | Bar.A
|  | Final Pressure | 4.284 | Bar.G
UVC with Air Bubble. (OSO, using commissioning valve)
|  | System or HWC capacity | 200 | Litres
|  | Expansion Vol | 50 | %
|  | Air Space Vol | 100 | Litres
|  | Water Volume | 100 | Litres
|  | Pre Charge Pressure | 0 | Bar.G
|  | Pre Charge Pressure | 1 | Bar.A
|  | Filling/supply Pressure | 3 | Bar.G
|  | Filling Pressure | 4 | Bar.A
|  | Air Space Vol | 25 | Litres
|  | Water Vol. Nominal | 175 | Litres
|  | Expansion % | 1.62 | %
|  | Expansion | 2.835 | Litres
|  | Water Volume | 177.835 | Litres
|  | Air Space Vol | 22.165 | Litres
|  | Final Pressure | 4.5116 | Bar.A
|  | Final Pressure | 3.5116 | Bar.G

## Sheet3
System or HWC capacity | 200 | Litres | System or HWC capacity | 200 | Litres |  | System or HWC capacity | 200 | Litres | System or HWC capacity | 200 | Litres
Expansion Vol | 25 | % | Expansion Vol | 10.45 | % |  | Expansion Vol | 100 | % | Expansion Vol | 10.45 | %
Air Space Vol | 50 | Litres | Air Space Vol | 20.9 | Litres | 29.1 | Air Space Vol | 200 | Litres | Air Space Vol | 20.9 | Litres | 179.1
Water Volume | 150 | Litres | Water Volume | 179.1 | Litres | -29.1 | Water Volume | 0 | Litres | Water Volume | 179.1 | Litres | -179.1
Pre Charge Pressure | 0 | Bar.G | Pre Charge Pressure | 0 | Bar.G |  | Pre Charge Pressure | 0 | Bar.G | Pre Charge Pressure | 0 | Bar.G
Pre Charge Pressure | 1 | Bar.A | Pre Charge Pressure | 1 | Bar.A |  | Pre Charge Pressure | 1 | Bar.A | Pre Charge Pressure | 1 | Bar.A
Filling/supply Pressure | 3 | Bar.G | Filling/supply Pressure | 3 | Bar.G |  | Filling/supply Pressure | 3 | Bar.G | Filling/supply Pressure | 3 | Bar.G
Filling Pressure | 4 | Bar.A | Filling Pressure | 4 | Bar.A |  | Filling Pressure | 4 | Bar.A | Filling Pressure | 4 | Bar.A
Air Space Vol | 12.5 | Litres | Air Space Vol | 5.225 | Litres | 7.275 | Air Space Vol | 50 | Litres | Air Space Vol | 5.225 | Litres | 44.775
Water Vol. Nominal | 187.5 | Litres | Water Vol. Nominal | 194.775 | Litres |  | Water Vol. Nominal | 150 | Litres | Water Vol. Nominal | 194.775 | Litres
Expansion % | 1.62 | % | Expansion % | 1.62 | % |  | Expansion % | 1.62 | % | Expansion % | 1.62 | %
Expansion | 2.43 | Litres | Expansion | 2.9014 | Litres |  | Expansion | 2.43 | Litres | Expansion | 3.1554 | Litres
Water Volume | 189.93 | Litres | Water Volume | 197.6764 | Litres | -7.7464 | Water Volume | 152.43 | Litres | Water Volume | 197.9304 | Litres | -45.5004
Air Space Vol | 10.07 | Litres | Air Space Vol | 2.3236 | Litres | 7.7464 | Air Space Vol | 47.57 | Litres | Air Space Vol | 2.0696 | Litres | 45.5004
Final Pressure | 4.9652 | Bar.A | Final Pressure | 8.9947 | Bar.A |  | Final Pressure | 4.2043 | Bar.A | Final Pressure | 10.0984 | Bar.A
Final Pressure | 3.9652 | Bar.G | Final Pressure | 7.9947 | Bar.G |  | Final Pressure | 3.2043 | Bar.G | Final Pressure | 9.0984 | Bar.G
Net HW | 150 | Litres | Net HW | 179.1 | Litres | -29.1 | Net HW | 0 | Litres | Net HW | 179.1 | Litres | -179.1
Unavailable HW | 39.93 | Litres | Unavailable HW | 18.5764 | Litres | 21.3536 | Unavailable HW | 152.43 | Litres | Unavailable HW | 18.8304 | Litres | 133.5996