## Sheet1
(From water at 15C) |  | Calcs based on Avg. of Flow&return hot water at 60C |  |  | values in yellow may be changed
Water |  | System or HWC capacity | 300 | Litres | S.sheet protected but not password protected
Temp | Exp | Vessel Capacity | 22 | Litres | Numbers in yellow may be changed.
Deg.C | % | Pre Charge Pressure | 3 | Bar.G | If s.sheet format needs changing, right click on "sheet1" (below left) and
50 | 1.124 | Pre Charge Pressure | 4 | Bar.A | select "unprotect sheet" from the drop down menu.
60 | 1.62 | Filling/supply Pressure | 3 | Bar.G
65 | 1.83 | Filling Pressure | 4 | Bar.A | Boiler Heating System
70 | 2.18 | Air Space Vol | 22 | Litres | Note: The pre pressure should never be higher than the filling pressure
75 | 2.48 | Reserve Water Vol | 0 | Litres | but where fitted to a boiler should be set 0.3/0.5 bar lower than the filling
80 | 2.8 | Expansion % | 1.83 | % | pressure as this gives a small water reserve when cold and avoids frequent
85 | 3.13 | Expansion | 5.49 | Litres | top ups. This must be taken into account when sizing the E.vessel.
90 | 3.49 | Water Space Vol | 5.49 | Litres
95 | 3.85 | Air Space Vol | 16.51 | Litres | When calculating the expansion volume %, use the average of the
100 | 4.24 | Final Pressure | 5.3301 | Bar.A | boiler flow&return temperatures.
105 | 4.64 | Final Pressure | 4.3301 | Bar.G
110 | 5.05 |  |  |  | Some boiler manufacturers now including Grant specify a
2.5 Bar PRV, this was normally 3.0 Bar, this must be taken
into account when sizing the expansion vessel.
NB: The filling pressure must not be lower than the pre charge pressure (the calculation
will also be incorrect ), it must always be = to or> than the pre charge pressure.