## Working Copy
Spreadsheet protected but not password protected, rightclick on Sheet1 and select unprotect to change any parameters
Values in Yellow may be changed with protection on.
GRANT Various Outputs 21L HEX |  |  | With External Buffer
Boiler Output | 41 | kw | Boiler Output | 41 | kw
Boiler HEX Vol | 21 | litres | External Buffer Vol | 50 | Litres
Boiler dT | 20 | Deg C | External Buffer dT | 15 | Deg C
Boiler buffering capacity | 0.48837 | kwh | External Buffer buffering capacity | 0.87209 | kwh
Heating Demand | 3 | kw | Heating Demand | 3 | kw
Boiler HEX recharging power | 38 | kw | Boiler Recharging Power | 38 | kw
Boiler Burner ON time | 0.77111 | mins | Boiler Burner ON time | 1.377 | mins
Boiler Burner OFF time | 9.7674 | mins | Boiler Burner OFF time | 17.4419 | mins
Boiler Burner Cycle Time | 10.5386 | mins | Boiler Burner Cycle Time | 18.8188 | mins
Boiler Average Burner Loading | 7.317% |  | Boiler Average Burner Loading | 7.317%
Boiler Output | 36 | kw | Boiler Output | 36 | kw
Boiler HEX Vol | 21 | litres | External Buffer Vol | 50 | Litres
Boiler dT | 20 | Deg C | External Buffer dT | 15 | Deg C
Boiler buffering capacity | 0.48837 | kwh | External Buffer buffering capacity | 0.87209 | kwh
Heating Demand | 3 | kw | Heating Demand | 3 | kw
Boiler HEX recharging power | 33 | kw | Boiler Recharging Power | 33 | kw
Boiler Burner ON time | 0.88795 | mins | Boiler Burner ON time | 1.5856 | mins
Boiler Burner OFF time | 9.7674 | mins | Boiler Burner OFF time | 17.4419 | mins
Cycle Time | 10.6554 | mins | Boiler Burner Cycle Time | 19.0275 | mins
Boiler Average Burner Loading | 8.333% |  | Boiler Average Burner Loading | 8.333%
Boiler Output | 26 | kw | Boiler Output | 26 | kw
Boiler HEX Vol | 21 | litres | External Buffer Vol | 50 | Litres
Boiler dT | 20 | Deg C | External Buffer dT | 15 | Deg C
Boiler buffering capacity | 0.48837 | kwh | External Buffer buffering capacity | 0.87209 | kwh
Heating Demand | 3 | kw | Heating Demand | 3 | kw
Boiler HEX recharging power | 23 | kw | Boiler Recharging Power | 23 | kw
Boiler Burner ON time | 1.274 | mins | Boiler Burner ON time | 2.275 | mins | 0.037917 | Hrs
Boiler Burner OFF time | 9.7674 | mins | Boiler Burner OFF time | 17.4419 | mins
Cycle Time | 11.0415 | mins | Boiler Burner Cycle Time | 19.7169 | mins | 0.32861 | Hrs
Boiler Average Burner Loading | 11.54% |  | Boiler Average Burner Loading | 11.54%