## Sheet1
Spreadsheet protected but not password protected, rightclick on Sheet1 and select unprotect to change any parameters
Values in Yellow may be changed with protection on.
Boiler Output | 12 | kw
Boiler HEX Vol | 18 | litres
Boiler dT | 10 | Deg C
Boiler buffering capacity | 0.2093 | kwh
Heating Demand | 2 | kw
Boiler HEX recharging power | 10 | kw
Boiler Burner ON time | 1.2558 | mins
Boiler Burner OFF time | 6.2791 | mins
Cycle Time | 7.5349 | mins
Boiler Burner ON time | 16.67%
Boiler Output | 12 | kw
Boiler HEX Vol | 18 | litres
Boiler dT | 10 | Deg C
Boiler buffering capacity | 0.2093 | kwh
Heating Demand | 5 | kw
Boiler HEX recharging power | 7 | kw
Boiler Burner ON time | 1.794 | mins
Boiler Burner OFF time | 2.5116 | mins
Cycle Time | 4.3056 | mins
Boiler Burner ON time | 41.67%
Boiler Output | 12 | kw
Boiler HEX Vol | 21 | litres
Boiler dT | 20 | Deg C
Boiler buffering capacity | 0.48837 | kwh
Heating Demand | 6 | kw
Boiler HEX recharging power | 6 | kw
Boiler Burner ON time | 4.8837 | mins
Boiler Burner OFF time | 4.8837 | mins
Cycle Time | 9.7674 | mins
Boiler Burner ON time | 50%
Boiler Output | 12 | kw
Boiler HEX Vol | 21 | litres
Boiler dT | 20 | Deg C
Boiler buffering capacity | 0.48837 | kwh
Heating Demand | 11.99 | kw
Boiler HEX recharging power | 0.01 | kw
Boiler Burner ON time | 2930.2326 | mins
Boiler Burner OFF time | 2.4439 | mins
Cycle Time | 2932.6765 | mins
Boiler Burner ON time | 99.92%