## Sheet1
Spreadsheet protected but not password protected, rightclick on Sheet1 and select unprotect to change any parameters
Values in Yellow may be changed with protection on.
GRANT Various Outputs 21L HEX |  |  | Warmflow 50kw 50L HEX
Boiler Output | 41 | kw | Boiler Output | 50 | kw
Boiler HEX Vol | 21 | litres | Boiler HEX Vol | 50 | litres
Boiler dT | 20 | Deg C | Boiler dT | 20 | Deg C
Boiler buffering capacity | 0.48837 | kwh | Boiler buffering capacity | 1.1628 | kwh
Heating Demand | 11.8 | kw | Heating Demand | 11.8 | kw
Boiler HEX recharging power | 29.2 | kw | Boiler HEX recharging power | 38.2 | kw
Boiler Burner ON time | 1.0035 | mins | Boiler Burner ON time | 1.8264 | mins
Boiler Burner OFF time | 2.4832 | mins | Boiler Burner OFF time | 5.9125 | mins
Cycle Time | 3.4868 | mins | Cycle Time | 7.7389 | mins
Boiler Average Burner Run | 28.78% |  | Boiler Average Burner Run | 23.6%
External Buffer Vol | 100 | Litres | External Buffer Vol | 100 | Litres
External Buffer dT | 15 | Deg C | External Buffer dT | 15 | Deg C
External Buffer buffering capacity | 1.7442 | kwh | External Buffer buffering capacity | 1.7442 | kwh
Boiler Burner ON time | 3.5839 | mins | Boiler Burner ON time | 2.7396 | mins
Boiler Burner OFF time | 8.8687 | mins | Boiler Burner OFF time | 8.8687 | mins
Cycle Time | 12.4527 | mins | Cycle Time | 11.6083 | mins
Boiler Average Burner Run | 28.78% | mins | Boiler Average Burner Run | 23.6% | mins
Boiler Output | 36 | kw
Boiler HEX Vol | 21 | litres
Boiler dT | 20 | Deg C
Boiler buffering capacity | 0.48837 | kwh
Heating Demand | 6.8 | kw
Boiler HEX recharging power | 29.2 | kw
Boiler Burner ON time | 1.0035 | mins
Boiler Burner OFF time | 4.3092 | mins
Cycle Time | 5.3127 | mins
Boiler Average Burner Run | 18.89%
External Buffer Vol | 100 | Litres
External Buffer dT | 15 | Deg C
External Buffer buffering capacity | 1.7442 | kwh
Boiler Burner ON time | 3.5839 | mins
Boiler Burner OFF time | 15.3899 | mins
Cycle Time | 18.9738 | mins
Boiler Average Burner Run | 18.89% | mins
Boiler Output | 26 | kw
Boiler HEX Vol | 21 | litres
Boiler dT | 20 | Deg C
Boiler buffering capacity | 0.48837 | kwh
Heating Demand | 1 | kw
Boiler HEX recharging power | 25 | kw
Boiler Burner ON time | 1.1721 | mins
Boiler Burner OFF time | 29.3023 | mins
Cycle Time | 30.4744 | mins
Boiler Average Burner Run | 3.846%
External Buffer Vol | 100 | Litres
External Buffer dT | 15 | Deg C
External Buffer buffering capacity | 1.7442 | kwh
Boiler Burner ON time | 4.186 | mins
Boiler Burner OFF time | 104.6512 | mins
Cycle Time | 108.8372 | mins
Boiler Average Burner Run | 3.846% | mins