## Calcs Gas Boiler
Dynamic
Pump
| Known | Known/Calc |  | Pump | Head | HEX | Res/Rad
| HEX | Rad |  | Speed | 2.1687 | 0.66907 | 1.4996 | M
| 1.74 | 3.9 |  | 62.01% |  | 12.9601 | 12.9601 | LPM
| 20.9 | 20.9
7M Typical Pump |  |  |  | Pump | Pump | Pump | Hex | Residual | Hex | Rads
|  |  | Pump | Head | Flow | Flow | dP | Head | Flow | Flow | Diff
M | LPM | LPH | Speed | M | LPM | LPH | M | M | LPM | LPM | LPM
6.9984 | 0 | 0 | 62.01% | 2.6911 | 0 | 0 | 0 | 2.6911 | 0 | 17.361 | 17.361
6.9984 | 4.32 | 259.2 | 62.01% | 2.6911 | 2.6788 | 160.7299 | 0.028586 | 2.6625 | 2.6788 | 17.2686 | 14.5897
6.9867 | 8.64 | 518.4 | 62.01% | 2.6866 | 5.3577 | 321.4598 | 0.11434 | 2.5722 | 5.3577 | 16.9734 | 11.6157
6.6485 | 12.96 | 777.6 | 62.01% | 2.5565 | 8.0365 | 482.1898 | 0.25727 | 2.2992 | 8.0365 | 16.0474 | 8.0109
6.1469 | 17.28 | 1036.8 | 62.01% | 2.3636 | 10.7153 | 642.9197 | 0.45737 | 1.9063 | 10.7153 | 14.6119 | 3.8966
5.5521 | 21.6 | 1296 | 62.01% | 2.1349 | 13.3942 | 803.6496 | 0.71464 | 1.4203 | 13.3942 | 12.6124 | -0.78175
5.3071 | 23.22 | 1393.2 | 62.01% | 2.0407 | 14.3987 | 863.9233 | 0.82586 | 1.2149 | 14.3987 | 11.6648 | -2.7339
4.9222 | 25.92 | 1555.2 | 62.01% | 1.8927 | 16.073 | 964.3795 | 1.0291 | 0.86362 | 16.073 | 9.835 | -6.2379
4.3157 | 30.24 | 1814.4 | 62.01% | 1.6595 | 18.7518 | 1125.1094 | 1.4007 | 0.25879 | 18.7518 | 5.3838 | -13.3681
Residual head at 100% pump speed&25LPM = 2.51, Second pump head requires 25LPM@5.59-2.51, 3.08M
Residual head at 100% pump speed&26LPM = 2.21, Second pump head requires 26LPM@6.04-2.21,3.83 M
Residual head at 100% pump speed&27LPM = 1.83, Second pump head requires 27LPM@6.52-1.83,4.69 M
| Residual head at 100% pump speed&27.5LPM = 1.68, Second pump head requires 27.5LPM@6.76-1.68, 5.08 M | [10 empty] | Dynamic Pump Head | 572mb
| Residual head at 100% pump speed&28LPM = 1.49, Second pump head requires 28LPM@7.01-1.49,5.52 M | [10 empty] | Residual Pump Head | 398mb | 174
| Residual head at 100% pump speed&30LPM = 0.75, Second pump head requires 30LPM@8.04-0.75, 7.29 M | [10 empty] | Flowrate | 20.89LPM
[7 empty] | Using | Using
[6 empty] | LLH | 8M UPS2 | 8M UPS2
|  |  | Boiler | Rads | Booster | Secondary | As a | As a
|  |  | CircPump | & system | Pump | Pump | Booster | LLH
|  |  | Residual | Required | Required | Required | Pump | Secondary
| Flow | Flow | Head | Head | Head | Head | Only | Pump
| m3/hr | LPM | M | M | M | M | Setting | Setting
| 1.5306 | 25 | 2.51 | 5.59 | 3.08 | 5.59 | PP1 | CC1
| 1.5919 | 26 | 2.21 | 6.04 | 3.83 | 6.04 | PP1 | CC1
| 1.6531 | 27 | 1.83 | 6.52 | 4.69 | 6.52 | PP2 | CC2
| 1.6837 | 27.5 | 1.68 | 6.76 | 5.08 | 6.76 | CC1 | CC2
| 1.7143 | 28 | 1.49 | 7.01 | 5.52 | 7.01 | CC1 | CC2
| 1.8368 | 30 | 0.75 | 8.04 | 7.29 | 8.04 | PP3 | CC3
Present Setup, 20.9LPM @ Rad(s) Head of 3.98M

## Calcs Oil Boiler
Dynamic
Pump
| Known | Known/Calc |  | Pump | Head | HEX | Res/Rad
| HEX | Rad |  | Speed | 5.26 | 0.12 | 5.14 | M
| 0.12 | 5.14 |  | 100% |  | 24 | 24 | LPM
| 24 | 24
7M Typical Pump |  |  |  | Pump | Pump | Pump | Hex | Residual | Hex | Rads
|  |  | Pump | Head | Flow | Flow | dP | Head | Flow | Flow | Diff
M | LPM | LPH | Speed | M | LPM | LPH | M | M | LPM | LPM | LPM
6.9984 | 0 | 0 | 100% | 6.9984 | 0 | 0 | 0 | 6.9984 | 0 | 28.0046 | 28.0046
6.9984 | 4.32 | 259.2 | 100% | 6.9984 | 4.32 | 259.2 | 0.003888 | 6.9945 | 4.32 | 27.9968 | 23.6768
6.9867 | 8.64 | 518.4 | 100% | 6.9867 | 8.64 | 518.4 | 0.015552 | 6.9712 | 8.64 | 27.9501 | 19.3101
6.6485 | 12.96 | 777.6 | 100% | 6.6485 | 12.96 | 777.6 | 0.034992 | 6.6135 | 12.96 | 27.2236 | 14.2636
6.1469 | 17.28 | 1036.8 | 100% | 6.1469 | 17.28 | 1036.8 | 0.062208 | 6.0847 | 17.28 | 26.1126 | 8.8326
5.5521 | 21.6 | 1296 | 100% | 5.5521 | 21.6 | 1296 | 0.0972 | 5.4549 | 21.6 | 24.7242 | 3.1242
5.3071 | 23.22 | 1393.2 | 100% | 5.3071 | 23.22 | 1393.2 | 0.11233 | 5.1948 | 23.22 | 24.1276 | 0.90758
4.9222 | 25.92 | 1555.2 | 100% | 4.9222 | 25.92 | 1555.2 | 0.13997 | 4.7822 | 25.92 | 23.1497 | -2.7703
4.3157 | 30.24 | 1814.4 | 100% | 4.3157 | 30.24 | 1814.4 | 0.19051 | 4.1252 | 30.24 | 21.5006 | -8.7394
[7 empty] | Using | Using
[6 empty] | LLH | 8M UPS2 | 8M UPS2
|  |  | Boiler | Rads | Booster | Secondary | As a | As a
|  |  | CircPump | & system | Pump | Pump | Booster | LLH
|  |  | Residual | Required | Required | Required | Pump | Secondary
| Flow | Flow | Head | Head | Head | Head | Only | Pump
| m3/hr | LPM | M | M | M | M | Setting | Setting
| 1.5306 | 25 | 2.51 | 5.59 | 3.08 | 5.59 | PP1 | CC1
| 1.5919 | 26 | 2.21 | 6.04 | 3.83 | 6.04 | PP1 | CC1
| 1.6531 | 27 | 1.83 | 6.52 | 4.69 | 6.52 | PP2 | CC2
| 1.6837 | 27.5 | 1.68 | 6.76 | 5.08 | 6.76 | CC1 | CC2
| 1.7143 | 28 | 1.49 | 7.01 | 5.52 | 7.01 | CC1 | CC2
| 1.8368 | 30 | 0.75 | 8.04 | 7.29 | 8.04 | PP3 | CC3
Present Setup, 20.9LPM @ Rad(s) Head of 3.98M

## Calcs JTC 6M Wilo
| 6M Wilo Yonos Pico |  |  |  | Dynamic |  |  |  |  | mine 3m=15lpm
Pump
| Known | Known/Calc |  | Pump | Head | HEX | Res/Rad
| HEX | Rad |  | Speed | 5.6794 | 0.087448 | 5.592 | M
| 0.075 | 4.796 |  | 108% |  | 20.5162 | 20.5162 | LPM
| 19 | 19
7M Typical Pump |  |  |  | Pump | Pump | Pump | Hex | Residual | Hex | Rads
|  |  | Pump | Head | Flow | Flow | dP | Head | Flow | Flow | Diff
M | LPM | LPH | Speed | M | LPM | LPH | M | M | LPM | LPM | LPM
5.9976 | 0 | 0 | 108% | 6.993 | 0 | 0 | 0 | 6.993 | 0 | 22.9428 | 22.9428
5.9976 | 3.9992 | 239.9526 | 108% | 6.993 | 4.3183 | 259.1008 | 0.0038743 | 6.9892 | 4.3183 | 22.9365 | 18.6181
5.9876 | 7.9984 | 479.9051 | 108% | 6.9814 | 8.6367 | 518.2015 | 0.015497 | 6.9659 | 8.6367 | 22.8983 | 14.2616
5.6977 | 11.9976 | 719.8577 | 108% | 6.6434 | 12.955 | 777.3023 | 0.034868 | 6.6085 | 12.955 | 22.3031 | 9.3481
5.2679 | 15.9968 | 959.8102 | 108% | 6.1422 | 17.2734 | 1036.4031 | 0.061988 | 6.0802 | 17.2734 | 21.3931 | 4.1197
4.7581 | 19.996 | 1199.7628 | 108% | 5.5478 | 21.5917 | 1295.5039 | 0.096857 | 5.451 | 21.5917 | 20.2558 | -1.3359
4.5482 | 21.4958 | 1289.745 | 108% | 5.3031 | 23.2111 | 1392.6667 | 0.11193 | 5.1911 | 23.2111 | 19.7672 | -3.4439
4.2183 | 23.9953 | 1439.7154 | 108% | 4.9184 | 25.9101 | 1554.6046 | 0.13947 | 4.779 | 25.9101 | 18.9662 | -6.9438
3.6985 | 27.9945 | 1679.6679 | 108% | 4.3124 | 30.2284 | 1813.7054 | 0.18984 | 4.1225 | 30.2284 | 17.6156 | -12.6129 | 6M | 3.7 | 27.99
[13 empty] | 3.2 | 41
[13 empty] | 2.7 | 35.8
[13 empty] | 2.2 | 41
[13 empty] | 1.7 | 46.5
[13 empty] | 1.2 | 53
[13 empty] | 0.7 | 58
[12 empty] | 7m | 4.3068 | 30.1732
[13 empty] | 3.7248 | 44.198
[13 empty] | 3.1428 | 38.5924
[13 empty] | 2.5608 | 44.198
[13 empty] | 1.9788 | 50.127
[13 empty] | 1.3968 | 57.134
[13 empty] | 0.8148 | 62.524
[7 empty] | Using | Using
[6 empty] | LLH | 8M UPS2 | 8M UPS2
|  |  | Boiler | Rads | Booster | Secondary | As a | As a
|  |  | CircPump | & system | Pump | Pump | Booster | LLH
|  |  | Residual | Required | Required | Required | Pump | Secondary
| Flow | Flow | Head | Head | Head | Head | Only | Pump
| m3/hr | LPM | M | M | M | M | Setting | Setting
| 1.5306 | 25 | 2.51 | 5.59 | 3.08 | 5.59 | PP1 | CC1
| 1.5919 | 26 | 2.21 | 6.04 | 3.83 | 6.04 | PP1 | CC1
| 1.6531 | 27 | 1.83 | 6.52 | 4.69 | 6.52 | PP2 | CC2
| 1.6837 | 27.5 | 1.68 | 6.76 | 5.08 | 6.76 | CC1 | CC2
| 1.7143 | 28 | 1.49 | 7.01 | 5.52 | 7.01 | CC1 | CC2
| 1.8368 | 30 | 0.75 | 8.04 | 7.29 | 8.04 | PP3 | CC3
Present Setup, 20.9LPM @ Rad(s) Head of 3.98M

## Various Speeds
[5 empty] | Dynamic |  | Spreadsheet Protected but not password protected. Cell P152 can be changed with protection on
Pump
| Known | Known/Calc |  | Pump | Head | HEX | Res/Rad
| HEX | Rads |  | Speed | 6.3867 | 2.9772 | 3.4094 | M |  | Hex resistance 3.1M at 20.0LPM
| 3.1 | 3.55 |  | 98% |  | 19.6 | 19.6 | LPM |  | Rads Resistance 3.553M at 20.0LPM. (Based on my own)
| 20 | 20 |  |  |  |  | 1176 | LPH
| Inputted from Cell P152 |  |  | Dynamic |  |  |  | Residual |  | Rads Flow
|  |  | Dynamic | Pump | Pump | Pump | Hex | Dynamic | Hex | Dynamic
|  |  | Head | Head | Flow | Flow | dP | 98% | Flow | 98% | Diff
M | LPM | LPH | Speed | M | LPM | LPH | M | M | LPM | LPM | LPM
6.9984 | 0 | 0 | 98% | 6.7213 | 0 | 0 | 0 | 6.7213 | 0 | 27.5195 | 27.5195
6.9984 | 4.32 | 259.2 | 98% | 6.7213 | 4.2336 | 254.016 | 0.13891 | 6.5824 | 4.2336 | 27.2337 | 23.0001
6.9867 | 8.64 | 518.4 | 98% | 6.7101 | 8.4672 | 508.032 | 0.55562 | 6.1544 | 8.4672 | 26.3336 | 17.8664
6.6485 | 12.96 | 777.6 | 98% | 6.3852 | 12.7008 | 762.048 | 1.2502 | 5.135 | 12.7008 | 24.054 | 11.3532
6.1469 | 17.28 | 1036.8 | 98% | 5.9035 | 16.9344 | 1016.064 | 2.2225 | 3.681 | 16.9344 | 20.3657 | 3.4313
5.5521 | 21.6 | 1296 | 98% | 5.3322 | 21.168 | 1270.08 | 3.4727 | 1.8595 | 21.168 | 14.475 | -6.693
5.3071 | 23.22 | 1393.2 | 98% | 5.097 | 22.7556 | 1365.336 | 4.0131 | 1.0839 | 22.7556 | 11.0511 | -11.7045
4.9222 | 25.92 | 1555.2 | 98% | 4.7273 | 25.4016 | 1524.096 | 5.0006 | -0.27333 | 25.4016 | #NUM! | #NUM!
4.3157 | 30.24 | 1814.4 | 98% | 4.1448 | 29.6352 | 1778.112 | 6.8064 | -2.6616 | 29.6352 | #NUM! | #NUM!
|  |  |  | Dynamic |  |  |  | Residual
|  |  | Dynamic | Pump | Pump | Pump | Hex | Head | Hex | Rads
|  |  | Head | Head | Flow | Flow | dP | 100% | Flow | Flow | Diff
M | LPM | LPH | Speed | M | LPM | LPH | M | M | LPM | LPM | LPM
6.9984 | 0 | 0 | 100% | 6.9984 | 0 | 0 | 0 | 6.9984 | 0 | 28.0812 | 28.0812
6.9984 | 4.32 | 259.2 | 1 | 6.9984 | 4.32 | 259.2 | 0.14463 | 6.8538 | 4.32 | 27.7895 | 23.4695
6.9867 | 8.64 | 518.4 | 1 | 6.9867 | 8.64 | 518.4 | 0.57853 | 6.4082 | 8.64 | 26.871 | 18.231
6.6485 | 12.96 | 777.6 | 1 | 6.6485 | 12.96 | 777.6 | 1.3017 | 5.3468 | 12.96 | 24.5449 | 11.5849
6.1469 | 17.28 | 1036.8 | 1 | 6.1469 | 17.28 | 1036.8 | 2.3141 | 3.8328 | 17.28 | 20.7813 | 3.5013
5.5521 | 21.6 | 1296 | 1 | 5.5521 | 21.6 | 1296 | 3.6158 | 1.9362 | 21.6 | 14.7704 | -6.8296
5.3071 | 23.22 | 1393.2 | 1 | 5.3071 | 23.22 | 1393.2 | 4.1786 | 1.1286 | 23.22 | 11.2766 | -11.9434
4.9222 | 25.92 | 1555.2 | 1 | 4.9222 | 25.92 | 1555.2 | 5.2068 | -0.2846 | 25.92 | #NUM! | #NUM!
4.3157 | 30.24 | 1814.4 | 1 | 4.3157 | 30.24 | 1814.4 | 7.087 | -2.7714 | 30.24 | #NUM! | #NUM!
|  |  |  | Dynamic |  |  |  | Residual
|  |  | Dynamic | Pump | Pump | Pump | Hex | Head | Hex | Rads
|  |  | Head | Head | Flow | Flow | dP | 80% | Flow | Flow | Diff
M | LPM | LPH | Speed | M | LPM | LPH | M | M | LPM | LPM | LPM
6.9984 | 0 | 0 | 80% | 4.479 | 0 | 0 | 0 | 4.479 | 0 | 22.4649 | 22.4649
6.9984 | 4.32 | 259.2 | 0.8 | 4.479 | 3.456 | 207.36 | 0.092566 | 4.3864 | 3.456 | 22.2316 | 18.7756
6.9867 | 8.64 | 518.4 | 0.8 | 4.4715 | 6.912 | 414.72 | 0.37026 | 4.1012 | 6.912 | 21.4968 | 14.5848
6.6485 | 12.96 | 777.6 | 0.8 | 4.255 | 10.368 | 622.08 | 0.83309 | 3.4219 | 10.368 | 19.6359 | 9.2679
6.1469 | 17.28 | 1036.8 | 0.8 | 3.934 | 13.824 | 829.44 | 1.481 | 2.453 | 13.824 | 16.6251 | 2.8011
5.5521 | 21.6 | 1296 | 0.8 | 3.5533 | 17.28 | 1036.8 | 2.3141 | 1.2392 | 17.28 | 11.8164 | -5.4636
5.3071 | 23.22 | 1393.2 | 0.8 | 3.3966 | 18.576 | 1114.56 | 2.6743 | 0.72228 | 18.576 | 9.0213 | -9.5547
4.9222 | 25.92 | 1555.2 | 0.8 | 3.1502 | 20.736 | 1244.16 | 3.3324 | -0.18215 | 20.736 | #NUM! | #NUM!
4.3157 | 30.24 | 1814.4 | 0.8 | 2.762 | 24.192 | 1451.52 | 4.5357 | -1.7737 | 24.192 | #NUM! | #NUM!
|  |  |  | Dynamic |  |  |  | Residual
|  |  | Dynamic | Pump | Pump | Pump | Hex | Head | Hex | Rads
|  |  | Head | Head | Flow | Flow | dP | 70% | Flow | Flow | Diff
M | LPM | LPH | Speed | M | LPM | LPH | M | M | LPM | LPM | LPM
6.9984 | 0 | 0 | 70% | 3.4292 | 0 | 0 | 0 | 3.4292 | 0 | 19.6568 | 19.6568
6.9984 | 4.32 | 259.2 | 0.7 | 3.4292 | 3.024 | 181.44 | 0.07087 | 3.3583 | 3.024 | 19.4526 | 16.4286
6.9867 | 8.64 | 518.4 | 0.7 | 3.4235 | 6.048 | 362.88 | 0.28348 | 3.14 | 6.048 | 18.8097 | 12.7617
6.6485 | 12.96 | 777.6 | 0.7 | 3.2578 | 9.072 | 544.32 | 0.63783 | 2.6199 | 9.072 | 17.1815 | 8.1095
6.1469 | 17.28 | 1036.8 | 0.7 | 3.012 | 12.096 | 725.76 | 1.1339 | 1.8781 | 12.096 | 14.5469 | 2.4509
5.5521 | 21.6 | 1296 | 0.7 | 2.7205 | 15.12 | 907.2 | 1.7718 | 0.94875 | 15.12 | 10.3393 | -4.7807
5.3071 | 23.22 | 1393.2 | 0.7 | 2.6005 | 16.254 | 975.24 | 2.0475 | 0.553 | 16.254 | 7.8936 | -8.3604
4.9222 | 25.92 | 1555.2 | 0.7 | 2.4119 | 18.144 | 1088.64 | 2.5513 | -0.13945 | 18.144 | #NUM! | #NUM!
4.3157 | 30.24 | 1814.4 | 0.7 | 2.1147 | 21.168 | 1270.08 | 3.4727 | -1.358 | 21.168 | #NUM! | #NUM!
|  |  |  | Dynamic |  |  |  | Residual
|  |  | Dynamic | Pump | Pump | Pump | Hex | Head | Hex | Rads
|  |  | Head | Head | Flow | Flow | dP | 60% | Flow | Flow | Diff
M | LPM | LPH | Speed | M | LPM | LPH | M | M | LPM | LPM | LPM
6.9984 | 0 | 0 | 60% | 2.5194 | 0 | 0 | 0 | 2.5194 | 0 | 16.8487 | 16.8487
6.9984 | 4.32 | 259.2 | 0.6 | 2.5194 | 2.592 | 155.52 | 0.052068 | 2.4674 | 2.592 | 16.6737 | 14.0817
6.9867 | 8.64 | 518.4 | 0.6 | 2.5152 | 5.184 | 311.04 | 0.20827 | 2.307 | 5.184 | 16.1226 | 10.9386
6.6485 | 12.96 | 777.6 | 0.6 | 2.3935 | 7.776 | 466.56 | 0.46861 | 1.9248 | 7.776 | 14.727 | 6.951
6.1469 | 17.28 | 1036.8 | 0.6 | 2.2129 | 10.368 | 622.08 | 0.83309 | 1.3798 | 10.368 | 12.4688 | 2.1008
5.5521 | 21.6 | 1296 | 0.6 | 1.9987 | 12.96 | 777.6 | 1.3017 | 0.69704 | 12.96 | 8.8623 | -4.0977
5.3071 | 23.22 | 1393.2 | 0.6 | 1.9106 | 13.932 | 835.92 | 1.5043 | 0.40628 | 13.932 | 6.766 | -7.166
4.9222 | 25.92 | 1555.2 | 0.6 | 1.772 | 15.552 | 933.12 | 1.8745 | -0.10246 | 15.552 | #NUM! | #NUM!
4.3157 | 30.24 | 1814.4 | 0.6 | 1.5536 | 18.144 | 1088.64 | 2.5513 | -0.99769 | 18.144 | #NUM! | #NUM!
|  |  |  | Dynamic |  |  |  | Residual
|  |  | Dynamic | Pump | Pump | Pump | Hex | Head | Hex | Rads
|  |  | Head | Head | Flow | Flow | dP | 53% | Flow | Flow | Diff
M | LPM | LPH | Speed | M | LPM | LPH | M | M | LPM | LPM | LPM
6.9984 | 0 | 0 | 53% | 1.9659 | 0 | 0 | 0 | 1.9659 | 0 | 14.883 | 14.883
6.9984 | 4.32 | 259.2 | 0.53 | 1.9659 | 2.2896 | 137.376 | 0.040628 | 1.9252 | 2.2896 | 14.7284 | 12.4388
6.9867 | 8.64 | 518.4 | 0.53 | 1.9626 | 4.5792 | 274.752 | 0.16251 | 1.8001 | 4.5792 | 14.2416 | 9.6624
6.6485 | 12.96 | 777.6 | 0.53 | 1.8676 | 6.8688 | 412.128 | 0.36565 | 1.5019 | 6.8688 | 13.0088 | 6.14
6.1469 | 17.28 | 1036.8 | 0.53 | 1.7267 | 9.1584 | 549.504 | 0.65004 | 1.0766 | 9.1584 | 11.0141 | 1.8557
5.5521 | 21.6 | 1296 | 0.53 | 1.5596 | 11.448 | 686.88 | 1.0157 | 0.54389 | 11.448 | 7.8283 | -3.6197
5.3071 | 23.22 | 1393.2 | 0.53 | 1.4908 | 12.3066 | 738.396 | 1.1738 | 0.31701 | 12.3066 | 5.9766 | -6.33
4.9222 | 25.92 | 1555.2 | 0.53 | 1.3826 | 13.7376 | 824.256 | 1.4626 | -0.079945 | 13.7376 | #NUM! | #NUM!
4.3157 | 30.24 | 1814.4 | 0.53 | 1.2123 | 16.0272 | 961.632 | 1.9908 | -0.77848 | 16.0272 | #NUM! | #NUM!
|  |  |  | Dynamic |  |  |  | Residual
|  |  | Dynamic | Pump | Pump | Pump | Hex | Head | Hex | Rads
|  |  | Head | Head | Flow | Flow | dP | 40% | Flow | Flow | Diff
M | LPM | LPH | Speed | M | LPM | LPH | M | M | LPM | LPM | LPM
6.9984 | 0 | 0 | 40% | 1.1197 | 0 | 0 | 0 | 1.1197 | 0 | 11.2325 | 11.2325
6.9984 | 4.32 | 259.2 | 0.4 | 1.1197 | 1.728 | 103.68 | 0.023141 | 1.0966 | 1.728 | 11.1158 | 9.3878
6.9867 | 8.64 | 518.4 | 0.4 | 1.1179 | 3.456 | 207.36 | 0.092566 | 1.0253 | 3.456 | 10.7484 | 7.2924
6.6485 | 12.96 | 777.6 | 0.4 | 1.0638 | 5.184 | 311.04 | 0.20827 | 0.85548 | 5.184 | 9.818 | 4.634
6.1469 | 17.28 | 1036.8 | 0.4 | 0.98351 | 6.912 | 414.72 | 0.37026 | 0.61325 | 6.912 | 8.3125 | 1.4005
5.5521 | 21.6 | 1296 | 0.4 | 0.88833 | 8.64 | 518.4 | 0.57853 | 0.3098 | 8.64 | 5.9082 | -2.7318
5.3071 | 23.22 | 1393.2 | 0.4 | 0.84914 | 9.288 | 557.28 | 0.66857 | 0.18057 | 9.288 | 4.5106 | -4.7774
4.9222 | 25.92 | 1555.2 | 0.4 | 0.78755 | 10.368 | 622.08 | 0.83309 | -0.045536 | 10.368 | #NUM! | #NUM!
4.3157 | 30.24 | 1814.4 | 0.4 | 0.69051 | 12.096 | 725.76 | 1.1339 | -0.44342 | 12.096 | #NUM! | #NUM!
|  |  |  | Dynamic |  |  |  | Residual
|  |  | Dynamic | Pump | Pump | Pump | Hex | Head | Hex | Rads
|  |  | Head | Head | Flow | Flow | dP | 30% | Flow | Flow | Diff
M | LPM | LPH | Speed | M | LPM | LPH | M | M | LPM | LPM | LPM
6.9984 | 0 | 0 | 30% | 0.62986 | 0 | 0 | 0 | 0.62986 | 0 | 8.4244 | 8.4244
6.9984 | 4.32 | 259.2 | 0.3 | 0.62986 | 1.296 | 77.76 | 0.013017 | 0.61684 | 1.296 | 8.3368 | 7.0408
6.9867 | 8.64 | 518.4 | 0.3 | 0.62881 | 2.592 | 155.52 | 0.052068 | 0.57674 | 2.592 | 8.0613 | 5.4693
6.6485 | 12.96 | 777.6 | 0.3 | 0.59836 | 3.888 | 233.28 | 0.11715 | 0.48121 | 3.888 | 7.3635 | 3.4755
6.1469 | 17.28 | 1036.8 | 0.3 | 0.55322 | 5.184 | 311.04 | 0.20827 | 0.34495 | 5.184 | 6.2344 | 1.0504
5.5521 | 21.6 | 1296 | 0.3 | 0.49969 | 6.48 | 388.8 | 0.32543 | 0.17426 | 6.48 | 4.4311 | -2.0489
5.3071 | 23.22 | 1393.2 | 0.3 | 0.47764 | 6.966 | 417.96 | 0.37607 | 0.10157 | 6.966 | 3.383 | -3.583
4.9222 | 25.92 | 1555.2 | 0.3 | 0.443 | 7.776 | 466.56 | 0.46861 | -0.025614 | 7.776 | #NUM! | #NUM!
4.3157 | 30.24 | 1814.4 | 0.3 | 0.38841 | 9.072 | 544.32 | 0.63783 | -0.24942 | 9.072 | #NUM! | #NUM!
|  |  |  | Dynamic |  |  |  | Residual
|  |  | Dynamic | Pump | Pump | Pump | Hex | Head | Hex | Rads
|  |  | Head | Head | Flow | Flow | dP | 20% | Flow | Flow | Diff
M | LPM | LPH | Speed | M | LPM | LPH | M | M | LPM | LPM | LPM
6.9984 | 0 | 0 | 20% | 0.27994 | 0 | 0 | 0 | 0.27994 | 0 | 5.6162 | 5.6162
6.9984 | 4.32 | 259.2 | 0.2 | 0.27994 | 0.864 | 51.84 | 0.0057853 | 0.27415 | 0.864 | 5.5579 | 4.6939
6.9867 | 8.64 | 518.4 | 0.2 | 0.27947 | 1.728 | 103.68 | 0.023141 | 0.25633 | 1.728 | 5.3742 | 3.6462
6.6485 | 12.96 | 777.6 | 0.2 | 0.26594 | 2.592 | 155.52 | 0.052068 | 0.21387 | 2.592 | 4.909 | 2.317
6.1469 | 17.28 | 1036.8 | 0.2 | 0.24588 | 3.456 | 207.36 | 0.092566 | 0.15331 | 3.456 | 4.1563 | 0.70027
5.5521 | 21.6 | 1296 | 0.2 | 0.22208 | 4.32 | 259.2 | 0.14463 | 0.077449 | 4.32 | 2.9541 | -1.3659
5.3071 | 23.22 | 1393.2 | 0.2 | 0.21228 | 4.644 | 278.64 | 0.16714 | 0.045143 | 4.644 | 2.2553 | -2.3887
4.9222 | 25.92 | 1555.2 | 0.2 | 0.19689 | 5.184 | 311.04 | 0.20827 | -0.011384 | 5.184 | #NUM! | #NUM!
4.3157 | 30.24 | 1814.4 | 0.2 | 0.17263 | 6.048 | 362.88 | 0.28348 | -0.11085 | 6.048 | #NUM! | #NUM!
[12 empty] | 98% | (changes cell E13)