## Calcs Gas Boiler
Dynamic
Pump
| Known | Known/Calc |  | Pump | Head | HEX | Res/Rad
| HEX | Rad |  | Speed | 2.1687 | 0.66907 | 1.4996 | M
| 1.74 | 3.9 |  | 62.01% |  | 12.9601 | 12.9601 | LPM
| 20.9 | 20.9
7M Typical Pump |  |  |  | Pump | Pump | Pump | Hex | Residual | Hex | Rads
|  |  | Pump | Head | Flow | Flow | dP | Head | Flow | Flow | Diff
M | LPM | LPH | Speed | M | LPM | LPH | M | M | LPM | LPM | LPM
6.9984 | 0 | 0 | 62.01% | 2.6911 | 0 | 0 | 0 | 2.6911 | 0 | 17.361 | 17.361
6.9984 | 4.32 | 259.2 | 62.01% | 2.6911 | 2.6788 | 160.7299 | 0.028586 | 2.6625 | 2.6788 | 17.2686 | 14.5897
6.9867 | 8.64 | 518.4 | 62.01% | 2.6866 | 5.3577 | 321.4598 | 0.11434 | 2.5722 | 5.3577 | 16.9734 | 11.6157
6.6485 | 12.96 | 777.6 | 62.01% | 2.5565 | 8.0365 | 482.1898 | 0.25727 | 2.2992 | 8.0365 | 16.0474 | 8.0109
6.1469 | 17.28 | 1036.8 | 62.01% | 2.3636 | 10.7153 | 642.9197 | 0.45737 | 1.9063 | 10.7153 | 14.6119 | 3.8966
5.5521 | 21.6 | 1296 | 62.01% | 2.1349 | 13.3942 | 803.6496 | 0.71464 | 1.4203 | 13.3942 | 12.6124 | -0.78175
5.3071 | 23.22 | 1393.2 | 62.01% | 2.0407 | 14.3987 | 863.9233 | 0.82586 | 1.2149 | 14.3987 | 11.6648 | -2.7339
4.9222 | 25.92 | 1555.2 | 62.01% | 1.8927 | 16.073 | 964.3795 | 1.0291 | 0.86362 | 16.073 | 9.835 | -6.2379
4.3157 | 30.24 | 1814.4 | 62.01% | 1.6595 | 18.7518 | 1125.1094 | 1.4007 | 0.25879 | 18.7518 | 5.3838 | -13.3681
Residual head at 100% pump speed&25LPM = 2.51, Second pump head requires 25LPM@5.59-2.51, 3.08M
Residual head at 100% pump speed&26LPM = 2.21, Second pump head requires 26LPM@6.04-2.21,3.83 M
Residual head at 100% pump speed&27LPM = 1.83, Second pump head requires 27LPM@6.52-1.83,4.69 M
| Residual head at 100% pump speed&27.5LPM = 1.68, Second pump head requires 27.5LPM@6.76-1.68, 5.08 M | [10 empty] | Dynamic Pump Head | 572mb
| Residual head at 100% pump speed&28LPM = 1.49, Second pump head requires 28LPM@7.01-1.49,5.52 M | [10 empty] | Residual Pump Head | 398mb | 174
| Residual head at 100% pump speed&30LPM = 0.75, Second pump head requires 30LPM@8.04-0.75, 7.29 M | [10 empty] | Flowrate | 20.89LPM
[7 empty] | Using | Using
[6 empty] | LLH | 8M UPS2 | 8M UPS2
|  |  | Boiler | Rads | Booster | Secondary | As a | As a
|  |  | CircPump | & system | Pump | Pump | Booster | LLH
|  |  | Residual | Required | Required | Required | Pump | Secondary
| Flow | Flow | Head | Head | Head | Head | Only | Pump
| m3/hr | LPM | M | M | M | M | Setting | Setting
| 1.5306 | 25 | 2.51 | 5.59 | 3.08 | 5.59 | PP1 | CC1
| 1.5919 | 26 | 2.21 | 6.04 | 3.83 | 6.04 | PP1 | CC1
| 1.6531 | 27 | 1.83 | 6.52 | 4.69 | 6.52 | PP2 | CC2
| 1.6837 | 27.5 | 1.68 | 6.76 | 5.08 | 6.76 | CC1 | CC2
| 1.7143 | 28 | 1.49 | 7.01 | 5.52 | 7.01 | CC1 | CC2
| 1.8368 | 30 | 0.75 | 8.04 | 7.29 | 8.04 | PP3 | CC3
Present Setup, 20.9LPM @ Rad(s) Head of 3.98M

## Calcs Oil Boiler
Dynamic
Pump
| Known | Known/Calc |  | Pump | Head | HEX | Res/Rad
| HEX | Rad |  | Speed | 5.26 | 0.12 | 5.14 | M
| 0.12 | 5.14 |  | 100% |  | 24 | 24 | LPM
| 24 | 24
7M Typical Pump |  |  |  | Pump | Pump | Pump | Hex | Residual | Hex | Rads
|  |  | Pump | Head | Flow | Flow | dP | Head | Flow | Flow | Diff
M | LPM | LPH | Speed | M | LPM | LPH | M | M | LPM | LPM | LPM
6.9984 | 0 | 0 | 100% | 6.9984 | 0 | 0 | 0 | 6.9984 | 0 | 28.0046 | 28.0046
6.9984 | 4.32 | 259.2 | 100% | 6.9984 | 4.32 | 259.2 | 0.003888 | 6.9945 | 4.32 | 27.9968 | 23.6768
6.9867 | 8.64 | 518.4 | 100% | 6.9867 | 8.64 | 518.4 | 0.015552 | 6.9712 | 8.64 | 27.9501 | 19.3101
6.6485 | 12.96 | 777.6 | 100% | 6.6485 | 12.96 | 777.6 | 0.034992 | 6.6135 | 12.96 | 27.2236 | 14.2636
6.1469 | 17.28 | 1036.8 | 100% | 6.1469 | 17.28 | 1036.8 | 0.062208 | 6.0847 | 17.28 | 26.1126 | 8.8326
5.5521 | 21.6 | 1296 | 100% | 5.5521 | 21.6 | 1296 | 0.0972 | 5.4549 | 21.6 | 24.7242 | 3.1242
5.3071 | 23.22 | 1393.2 | 100% | 5.3071 | 23.22 | 1393.2 | 0.11233 | 5.1948 | 23.22 | 24.1276 | 0.90758
4.9222 | 25.92 | 1555.2 | 100% | 4.9222 | 25.92 | 1555.2 | 0.13997 | 4.7822 | 25.92 | 23.1497 | -2.7703
4.3157 | 30.24 | 1814.4 | 100% | 4.3157 | 30.24 | 1814.4 | 0.19051 | 4.1252 | 30.24 | 21.5006 | -8.7394
[7 empty] | Using | Using
[6 empty] | LLH | 8M UPS2 | 8M UPS2
|  |  | Boiler | Rads | Booster | Secondary | As a | As a
|  |  | CircPump | & system | Pump | Pump | Booster | LLH
|  |  | Residual | Required | Required | Required | Pump | Secondary
| Flow | Flow | Head | Head | Head | Head | Only | Pump
| m3/hr | LPM | M | M | M | M | Setting | Setting
| 1.5306 | 25 | 2.51 | 5.59 | 3.08 | 5.59 | PP1 | CC1
| 1.5919 | 26 | 2.21 | 6.04 | 3.83 | 6.04 | PP1 | CC1
| 1.6531 | 27 | 1.83 | 6.52 | 4.69 | 6.52 | PP2 | CC2
| 1.6837 | 27.5 | 1.68 | 6.76 | 5.08 | 6.76 | CC1 | CC2
| 1.7143 | 28 | 1.49 | 7.01 | 5.52 | 7.01 | CC1 | CC2
| 1.8368 | 30 | 0.75 | 8.04 | 7.29 | 8.04 | PP3 | CC3
Present Setup, 20.9LPM @ Rad(s) Head of 3.98M

## Calcs JTC 6M Wilo
| 6M Wilo Yonos Pico |  |  |  | Dynamic |  |  |  |  | mine 3m=15lpm
Pump
| Known | Known/Calc |  | Pump | Head | HEX | Res/Rad
| HEX | Rad |  | Speed | 5.6794 | 0.087448 | 5.592 | M
| 0.075 | 4.796 |  | 108% |  | 20.5162 | 20.5162 | LPM
| 19 | 19
7M Typical Pump |  |  |  | Pump | Pump | Pump | Hex | Residual | Hex | Rads
|  |  | Pump | Head | Flow | Flow | dP | Head | Flow | Flow | Diff
M | LPM | LPH | Speed | M | LPM | LPH | M | M | LPM | LPM | LPM
5.9976 | 0 | 0 | 108% | 6.993 | 0 | 0 | 0 | 6.993 | 0 | 22.9428 | 22.9428
5.9976 | 3.9992 | 239.9526 | 108% | 6.993 | 4.3183 | 259.1008 | 0.0038743 | 6.9892 | 4.3183 | 22.9365 | 18.6181
5.9876 | 7.9984 | 479.9051 | 108% | 6.9814 | 8.6367 | 518.2015 | 0.015497 | 6.9659 | 8.6367 | 22.8983 | 14.2616
5.6977 | 11.9976 | 719.8577 | 108% | 6.6434 | 12.955 | 777.3023 | 0.034868 | 6.6085 | 12.955 | 22.3031 | 9.3481
5.2679 | 15.9968 | 959.8102 | 108% | 6.1422 | 17.2734 | 1036.4031 | 0.061988 | 6.0802 | 17.2734 | 21.3931 | 4.1197
4.7581 | 19.996 | 1199.7628 | 108% | 5.5478 | 21.5917 | 1295.5039 | 0.096857 | 5.451 | 21.5917 | 20.2558 | -1.3359
4.5482 | 21.4958 | 1289.745 | 108% | 5.3031 | 23.2111 | 1392.6667 | 0.11193 | 5.1911 | 23.2111 | 19.7672 | -3.4439
4.2183 | 23.9953 | 1439.7154 | 108% | 4.9184 | 25.9101 | 1554.6046 | 0.13947 | 4.779 | 25.9101 | 18.9662 | -6.9438
3.6985 | 27.9945 | 1679.6679 | 108% | 4.3124 | 30.2284 | 1813.7054 | 0.18984 | 4.1225 | 30.2284 | 17.6156 | -12.6129 | 6M | 3.7 | 27.99
[13 empty] | 3.2 | 41
[13 empty] | 2.7 | 35.8
[13 empty] | 2.2 | 41
[13 empty] | 1.7 | 46.5
[13 empty] | 1.2 | 53
[13 empty] | 0.7 | 58
[12 empty] | 7m | 4.3068 | 30.1732
[13 empty] | 3.7248 | 44.198
[13 empty] | 3.1428 | 38.5924
[13 empty] | 2.5608 | 44.198
[13 empty] | 1.9788 | 50.127
[13 empty] | 1.3968 | 57.134
[13 empty] | 0.8148 | 62.524
[7 empty] | Using | Using
[6 empty] | LLH | 8M UPS2 | 8M UPS2
|  |  | Boiler | Rads | Booster | Secondary | As a | As a
|  |  | CircPump | & system | Pump | Pump | Booster | LLH
|  |  | Residual | Required | Required | Required | Pump | Secondary
| Flow | Flow | Head | Head | Head | Head | Only | Pump
| m3/hr | LPM | M | M | M | M | Setting | Setting
| 1.5306 | 25 | 2.51 | 5.59 | 3.08 | 5.59 | PP1 | CC1
| 1.5919 | 26 | 2.21 | 6.04 | 3.83 | 6.04 | PP1 | CC1
| 1.6531 | 27 | 1.83 | 6.52 | 4.69 | 6.52 | PP2 | CC2
| 1.6837 | 27.5 | 1.68 | 6.76 | 5.08 | 6.76 | CC1 | CC2
| 1.7143 | 28 | 1.49 | 7.01 | 5.52 | 7.01 | CC1 | CC2
| 1.8368 | 30 | 0.75 | 8.04 | 7.29 | 8.04 | PP3 | CC3
Present Setup, 20.9LPM @ Rad(s) Head of 3.98M

## Dynamic
[5 empty] | Dynamic |  |  |  |  | Spreadsheet Protected but not password protected.
[5 empty] | Pump |  |  |  |  | Values in yellow may be changed with protection on..
| Known | Known |  | Pump | Head | HEX | Res/Rad
| HEX | Rads |  | Speed | 2.0854 | 0.97216 | 1.1133 | M |  | Vaillant Hex resistance 3.1M at 20.0LPM
M | 3.1 | 3.55 |  | 56% |  | 11.2 | 11.2 | LPM |  | Rads Resistance 3.553M at 20.0LPM. (Based on my own)
LPM | 20 | 20
| Input from Cell P30 |  |  | Dynamic |  |  |  | Residual |  | Rads Flow
|  |  | Dynamic | Pump | Pump | Pump | Hex | Dynamic | Hex | Dynamic
|  |  | Head | Head | Flow | Flow | dP | 56% | Flow | 56% | Diff
M | LPM | LPH | Speed | M | LPM | LPH | M | M | LPM | LPM | LPM
6.9984 | 0 | 0 | 56% | 2.1947 | 0 | 0 | 0 | 2.1947 | 0 | 15.7255 | 15.7255
6.9984 | 4.32 | 259.2 | 56% | 2.1947 | 2.4192 | 145.152 | 0.045357 | 2.1493 | 2.4192 | 15.5621 | 13.1429
6.9867 | 8.64 | 518.4 | 56% | 2.191 | 4.8384 | 290.304 | 0.18143 | 2.0096 | 4.8384 | 15.0478 | 10.2094
6.6485 | 12.96 | 777.6 | 56% | 2.085 | 7.2576 | 435.456 | 0.40821 | 1.6767 | 7.2576 | 13.7452 | 6.4876
6.1469 | 17.28 | 1036.8 | 56% | 1.9277 | 9.6768 | 580.608 | 0.72571 | 1.202 | 9.6768 | 11.6375 | 1.9607
5.5521 | 21.6 | 1296 | 56% | 1.7411 | 12.096 | 725.76 | 1.1339 | 0.6072 | 12.096 | 8.2714 | -3.8246
5.3071 | 23.22 | 1393.2 | 56% | 1.6643 | 13.0032 | 780.192 | 1.3104 | 0.35392 | 13.0032 | 6.3149 | -6.6883
4.9222 | 25.92 | 1555.2 | 56% | 1.5436 | 14.5152 | 870.912 | 1.6329 | -0.089251 | 14.5152 | #NUM! | #NUM!
4.3157 | 30.24 | 1814.4 | 56% | 1.3534 | 16.9344 | 1016.064 | 2.2225 | -0.8691 | 16.9344 | #NUM! | #NUM!
Pump
Speed
[12 empty] | 56% | (changes cell E13)