## Calcs
Rads balanced at 48C to give a dT of 10C. (flowrate = 0.522LPM/kw)
| Rad(S) Rated |  |  | Room | [5 empty] | Rad
Required | Output "50 Deg Rad" |  | Flo Temp | Temp | Ret Temp | Flow | Flow | DeltaT |  | Output
Output | KW | "Deg rad" | Deg C | Deg C | Deg C | LPM | M3/hr | Deg C | output | KW
36.44% | 1 | 22.9997 | 48 | 20 | 37.9994 | 0.52228 | 0.031349 | 10.0006 | 36.44% | 0.3644
| Rad(S) Rated |  |  | Room | [5 empty] | Rad
Required | Output "50 Deg Rad" |  | Flo Temp | Temp | Ret Temp | Flow | Flow | DeltaT |  | Output
Output | KW | "Deg rad" | Deg C | Deg C | Deg C | LPM | M3/hr | Deg C | output | KW
50% | 1 | 29.3365 | 56.2 | 20 | 42.473 | 0.52209 | 0.031338 | 13.727 | 50% | 0.5
| Rad(S) Rated |  |  | Room | [5 empty] | Rad
Required | Output "50 Deg Rad" |  | Flo Temp | Temp | Ret Temp | Flow | Flow | DeltaT |  | Output
Output | KW | "Deg rad" | Deg C | Deg C | Deg C | LPM | M3/hr | Deg C | output | KW
75% | 1 | 40.0741 | 70.4 | 20 | 49.7481 | 0.52053 | 0.031245 | 20.6519 | 75% | 0.75
| Rad(S) Rated |  |  | Room | [5 empty] | Rad
Required | Output "50 Deg Rad" |  | Flo Temp | Temp | Ret Temp | Flow | Flow | DeltaT |  | Output
Output | KW | "Deg rad" | Deg C | Deg C | Deg C | LPM | M3/hr | Deg C | output | KW
92.9% | 1 | 47.2462 | 80 | 20 | 54.4924 | 0.52203 | 0.031334 | 25.5076 | 92.9% | 0.929

## Copy of Calcs
Rads balanced at 48C to give a dT of 10C. (flowrate = 0.522LPM/kw)
| Rad(S) Rated |  |  | Room | [5 empty] | Rad
Required | Output "50 Deg Rad" |  | Flo Temp | Temp | Ret Temp | Flow | Flow | DeltaT |  | Output
Output | KW | "Deg rad" | Deg C | Deg C | Deg C | LPM | M3/hr | Deg C | output | KW
36.44% | 1 | 22.9997 | 48 | 20 | 37.9994 | 0.52228 | 0.031349 | 10.0006 | 36.44% | 0.3644
| Rad(S) Rated |  |  | Room | [5 empty] | Rad
Required | Output "50 Deg Rad" |  | Flo Temp | Temp | Ret Temp | Flow | Flow | DeltaT |  | Output
Output | KW | "Deg rad" | Deg C | Deg C | Deg C | LPM | M3/hr | Deg C | output | KW
50% | 1 | 29.3365 | 56.2 | 20 | 42.473 | 0.52209 | 0.031338 | 13.727 | 50% | 0.5
| Rad(S) Rated |  |  | Room | [5 empty] | Rad
Required | Output "50 Deg Rad" |  | Flo Temp | Temp | Ret Temp | Flow | Flow | DeltaT |  | Output
Output | KW | "Deg rad" | Deg C | Deg C | Deg C | LPM | M3/hr | Deg C | output | KW
75% | 1 | 40.0741 | 70.4 | 20 | 49.7481 | 0.52053 | 0.031245 | 20.6519 | 75% | 0.75
| Rad(S) Rated |  |  | Room | [5 empty] | Rad
Required | Output "50 Deg Rad" |  | Flo Temp | Temp | Ret Temp | Flow | Flow | DeltaT |  | Output
Output | KW | "Deg rad" | Deg C | Deg C | Deg C | LPM | M3/hr | Deg C | output | KW
92.9% | 1 | 47.2462 | 80 | 20 | 54.4924 | 0.52203 | 0.031334 | 25.5076 | 92.9% | 0.929