## Sheet1
Spreadsheet protected but not password protected
(From water at 15C) |  | Calcs based on Avg. of Flow&return hot water at 65C |  |  | Values in yellow may be changed.
Water |  | System or HWC capacity | 150 | Litres
Temp | Exp | Vessel Capacity | 14 | Litres | Boiler Heating System
Deg.C | % | Pre Charge Pressure | 1 | Bar.G | Note: The pre pressure should never be higher than the filling pressure
50 | 1.124 | Pre Charge Pressure | 2 | Bar.A | but where fitted to a boiler should be set 0.3/0.5 bar lower than the filling
60 | 1.62 | Filling/supply Pressure | 1.5 | Bar.G | pressure as this gives a small water reserve when cold and avoids frequent
65 | 1.83 | Filling Pressure | 2.5 | Bar.A | top ups. This must be taken into account when sizing the E.vessel.
70 | 2.18 | Air Space Vol | 11.2 | Litres
75 | 2.48 | Reserve Water Vol | 2.8 | Litres | When calculating the expansion volume %, use the average of the
80 | 2.8 | Expansion % | 1.83 | % | boiler flow&return temperatures.
85 | 3.13 | Expansion | 2.745 | Litres
90 | 3.49 | Water Space Vol | 5.545 | Litres | Some boiler manufacturers now including Grant specify a
95 | 3.85 | Air Space Vol | 8.455 | Litres | 2.5 Bar PRV, this was normally 3.0 Bar, this must be taken
100 | 4.24 | Final Pressure | 3.3116 | Bar.A | into account when sizing the expansion vessel.
105 | 4.64 | Final Pressure | 2.3116 | Bar.G
110 | 5.05 |  |  |  | NB: The filling pressure must not be lower than the pre charge pressure (the calculation
will also be incorrect ), it must always be = to or> than the pre charge pressure.