## Calcs
Design
Minimum
| OAT | -5 | Deg C
Design
| Room Temp | 20 | Deg C
| Range | 25 | Deg C
|  | Rad(S) Rated |  |  | Room | [5 empty] | Rad
OAT | Required | Output "50 Deg Rad" |  | Flo Temp | Temp | Ret Temp | Flow | Flow | DeltaT |  | Output
Deg C | Output | KW | "Deg rad" | Deg C | Deg C | Deg C | LPM | M3/hr | Deg C | output | KW
-1 | 84% | 1 | 43.7243 | 67.93 | 20 | 59.5187 | 1.4314 | 0.085919 | 8.4113 | 84% | 0.84
|  | Rad(S) Rated |  |  | Room | [5 empty] | Rad
OAT | Required | Output "50 Deg Rad" |  | Flo Temp | Temp | Ret Temp | Flow | Flow | DeltaT |  | Output
Deg C | Output | KW | "Deg rad" | Deg C | Deg C | Deg C | LPM | M3/hr | Deg C | output | KW
10.91 | 36.36% | 1 | 22.9609 | 44.78 | 20 | 41.1417 | 1.4324 | 0.085981 | 3.6383 | 36.36% | 0.3636
|  | Rad(S) Rated |  |  | Room | [5 empty] | Rad
OAT | Required | Output "50 Deg Rad" |  | Flo Temp | Temp | Ret Temp | Flow | Flow | DeltaT |  | Output
Deg C | Output | KW | "Deg rad" | Deg C | Deg C | Deg C | LPM | M3/hr | Deg C | output | KW
5 | 60% | 1 | 33.7534 | 56.76 | 20 | 50.7467 | 1.4302 | 0.085845 | 6.0133 | 60% | 0.6
|  | Rad(S) Rated |  |  | Room | [5 empty] | Rad
OAT | Required | Output "50 Deg Rad" |  | Flo Temp | Temp | Ret Temp | Flow | Flow | DeltaT |  | Output
Deg C | Output | KW | "Deg rad" | Deg C | Deg C | Deg C | LPM | M3/hr | Deg C | output | KW
0 | 80% | 1 | 42.1137 | 66.11 | 20 | 58.1175 | 1.4347 | 0.086115 | 7.9925 | 80% | 0.8
|  | Rad(S) Rated |  |  | Room | [5 empty] | Rad
OAT | Required | Output "50 Deg Rad" |  | Flo Temp | Temp | Ret Temp | Flow | Flow | DeltaT |  | Output
Deg C | Output | KW | "Deg rad" | Deg C | Deg C | Deg C | LPM | M3/hr | Deg C | output | KW
-5 | 100% | 1 | 50 | 75 | 20 | 65 | 1.4333 | 0.086034 | 10 | 100% | 1
Flow Rate reduced from 1.413LPM to 0.717LPM to give dT of 20C at 100% boiler output
|  | Rad(S) Rated |  |  | Room | [5 empty] | Rad
OAT | Required | Output "50 Deg Rad" |  | Flo Temp | Temp | Ret Temp | Flow | Flow | DeltaT |  | Output
Deg C | Output | KW | "Deg rad" | Deg C | Deg C | Deg C | LPM | M3/hr | Deg C | output | KW
-5 | 100% | 1 | 50 | 80 | 20 | 60 | 0.71667 | 0.043017 | 20 | 100% | 1
Originl flowrate of 1.43LPM
|  | Rad(S) Rated |  |  | Room | [5 empty] | Rad
OAT | Required | Output "50 Deg Rad" |  | Flo Temp | Temp | Ret Temp | Flow | Flow | DeltaT |  | Output
Deg C | Output | KW | "Deg rad" | Deg C | Deg C | Deg C | LPM | M3/hr | Deg C | output | KW
10.91 | 36.36% | 1 | 22.9609 | 44.78 | 20 | 41.1417 | 1.4324 | 0.085981 | 3.6383 | 36.36% | 0.3636
Flowrate reduced to 0.717LPM
|  | Rad(S) Rated |  |  | Room | [5 empty] | Rad
OAT | Required | Output "50 Deg Rad" |  | Flo Temp | Temp | Ret Temp | Flow | Flow | DeltaT |  | Output
Deg C | Output | KW | "Deg rad" | Deg C | Deg C | Deg C | LPM | M3/hr | Deg C | output | KW
10.91 | 36.36% | 1 | 22.9609 | 46.595 | 20 | 39.3267 | 0.71704 | 0.043039 | 7.2683 | 36.36% | 0.3636

## Copy of Calcs
Design
Minimum
| OAT | -5 | Deg C
Design
| Room Temp | 20 | Deg C
| Range | 25 | Deg C
|  | Rad(S) Rated |  |  | Room | [5 empty] | Rad
OAT | Required | Output "50 Deg Rad" |  | Flo Temp | Temp | Ret Temp | Flow | Flow | DeltaT |  | Output
Deg C | Output | KW | "Deg rad" | Deg C | Deg C | Deg C | LPM | M3/hr | Deg C | output | KW
-5 | 100% | 1 | 50 | 75 | 20 | 65 | 1.4333 | 0.086034 | 10 | 100% | 1
|  | Rad(S) Rated |  |  | Room | [5 empty] | Rad
OAT | Required | Output "50 Deg Rad" |  | Flo Temp | Temp | Ret Temp | Flow | Flow | DeltaT |  | Output
Deg C | Output | KW | "Deg rad" | Deg C | Deg C | Deg C | LPM | M3/hr | Deg C | output | KW
10.91 | 36.36% | 1 | 22.9609 | 44.78 | 20 | 41.1417 | 1.4324 | 0.085981 | 3.6383 | 36.36% | 0.3636
|  | Rad(S) Rated |  |  | Room | [5 empty] | Rad
OAT | Required | Output "50 Deg Rad" |  | Flo Temp | Temp | Ret Temp | Flow | Flow | DeltaT |  | Output
Deg C | Output | KW | "Deg rad" | Deg C | Deg C | Deg C | LPM | M3/hr | Deg C | output | KW
5 | 60% | 1 | 33.7534 | 56.76 | 20 | 50.7467 | 1.4302 | 0.085845 | 6.0133 | 60% | 0.6
|  | Rad(S) Rated |  |  | Room | [5 empty] | Rad
OAT | Required | Output "50 Deg Rad" |  | Flo Temp | Temp | Ret Temp | Flow | Flow | DeltaT |  | Output
Deg C | Output | KW | "Deg rad" | Deg C | Deg C | Deg C | LPM | M3/hr | Deg C | output | KW
0 | 80% | 1 | 42.1137 | 66.11 | 20 | 58.1175 | 1.4347 | 0.086115 | 7.9925 | 80% | 0.8